## Slide 1: ICF-IID Attic Fire Safety Requirement
Presenter’s Name: Donald Howard
Presenter’s Title: Health Insurance Specialist
CMS Division: Division of Continuing Care Providers
Notes: Welcome to the CMS webinar on the National Fire Protection Association’s (NFPA) attic fire protection requirements for Intermediate Care Facilities for Individual with Intellectual Disabilities otherwise know as ICF-IID.
My name is Don Howard. I am the ICF/IID co-lead from the CMS Central Office Division of Continuing Care Providers (DCCP) and will be providing you with information to allow for a better understand these NFPA requirements, which have been incorporated in to CMS regulation.
Please remember to take note of any questions you may have as we will provide a mailbox address at the end of the presentation where you may submit questions.

## Slide 2: Disclaimers
This presentation was prepared as a tool to assist providers and is not intended to grant rights or impose obligations. Although every reasonable effort has been made to assure the accuracy of the information within these slides, the ultimate responsibility for the correct submission of claims and response to any remittance advice lies with the provider of services.
This publication is a general summary that explains certain aspects of the Medicare Program, but is not a legal document. The official Medicare Program provisions are contained in the relevant laws, regulations, and rulings. Medicare policy changes frequently, and links to the source documents have been provided within the slides for your reference
The Centers for Medicare & Medicaid Services (CMS) employees, agents, and staff make no representation, warranty, or guarantee that this compilation of Medicare information is error-free and will bear no responsibility or liability for the results or consequences of the use of this guide.
Notes: Please be aware that there are disclaimers associated with this presentation.
Read slide.

## Slide 3: Learning Objectives
At the conclusion of this presentation, the participant will be able to understand :
  Regulatory requirements
  Attic protection requirements for occupied or used attic spaces
  Attic protection requirements for unoccupied or unused attic spaces
  Life Safety Code waiver
Notes: By the end of this presentation we hope that you will have a better understanding of:
The CMS regulatory requirements associated with attic fire protection;
The NFPA fire protection requirements associated with attics that are occupied and those that are unoccupied or unused; and
The ability for certain ICF-IID facilities to request a LSC waiver.

## Slide 4: Life Safety Code Final Rule
Final rule (CMS-3277-F) was published May 4, 2016 & effective July 5, 2016. https://www.gpo.gov/fdsys/pkg/FR-2016-05-04/pdf/2016-10043.pdf
The final rule updated fire safety requirements for certain providers including intermediate care facilities for individuals with intellectual disabilities (ICF-IID).
The final rule adopted the 2012 editions of the National Fire Protection Association's (NFPA) Life Safety Code (LSC) and Health Care Facilities Code.
Notes: CMS published a final rule (Docket Number CMS-3277-F) entitled Fire Safety Requirements for Certain Health Care Facilities, which includes fire safety requirements for ICF-IID facilities. This final rule updated the fire protection requirements for ICF-IID and specifically requires these facilities to comply with the 2012 editions of the National Fire Protection Association (or NFPA) Life Safety Code and Health Care Facilities Code.
If you would like to reference the specific sections of this final rule that apply to ICF-IID fire protection, please use the link provided in the slide under bullet number one. Navigate to page 26700 in the final rule and reference the regulatory requirements under 42 CFR 483.470 Condition of Participation for Physical Environment.

## Slide 5: Life Safety Code Attic Fire Safety Requirement
LSC was adopted by CMS regulation effective July 5, 2016.
Regulation gave ICF-IID until July 5, 2019 to comply with attic fire protection requirements.
Beginning July 5, 2019, an ICF-IID must be in compliance with Chapter 33.2.3.5.7.1, Sprinklers in attics, or Chapter 33.2.3.5.7.2, Heat detection systems in attics of the Life Safety Code.
Notes: The CMS regulation that requires certified health care facilities to comply with the 2012 edition of the Life Safety Code (or LSC) became effective on July 5, 2016. The 2012 edition of the LSC contains new provisions incorporated to protect the attics in both new and existing ICF-IIDs from fire. These new attic fire protection requirements would have been effective on July 5, 2016, however CMS recognized that existing ICF-IID facilities would need more time to install these new attic fire protection features. Therefore, CMS regulation provided an additional three years from the effective date of the regulation and required existing ICF-IID facilities to be in compliance with the new NFPA attic fire protection requirements by July 5, 2019.

## Slide 6: Automatic Sprinkler Requirement & Attic Used
Section 33.2.3.5.7.1 of the NFPA 101:
ICFs-IID where an automatic sprinkler system is installed, as required by LSC, and the attic is used for living purposes, storage, or fuel-fired equipment:
  Attic, shall be protected with automatic sprinklers that are part of the required, approved automatic sprinkler system in accordance with 9.7.1.1 of the LSC.
Notes: The requirements for ICF-IID attic fire protection can be found in the 2012 edition of the LSC in the Residential Board and Care Occupancies Chapters 32 and 33 under the Extinguishing Requirements sections. In ICF-IIDs where the LSC requires the facility to have an approved automatic sprinkler system, the sprinkler system must also protect attics that are being used for living purposes, storage, or fuel-fired equipment such as furnaces, boilers, hot water heaters, etc.

## Slide 7: Automatic Sprinkler Requirement & Attic Not Used
Section 33.2.3.5.7.2 of the NFPA 101:
ICFs/IID where an automatic sprinkler system is installed, as required by the LSC, and the attic is not used for living purposes, storage, or fuel-fired equipment:
  Attic, shall meet one of the following criteria:
Notes: In ICF-IIDs where the LSC requires the facility to have an approved automatic sprinkler system, but the attic is not used for living purposes, storage, or fuel-fired equipment, attic fire protection can be achieved meeting one of the following criteria:

## Slide 8: Attic Criteria
Attics shall be protected with automatic sprinklers that are part of the required, approved automatic sprinkler system in accordance with 9.7.1.1 of the LSC.
or
Attics shall be protected throughout by a heat detection system arranged to activate the building fire alarm system in accordance with Section 9.6 of the LSC.
or
Notes: In attics not used for living purposes, storage, or fuel-fired equipment, attic fire protection can be achieved by protecting the attic with automatic sprinklers that are part of the LSC required automatic sprinkler system, as would be required if the space were used for living purposes, storage, or fuel-fired equipment.
Alternately, attics not used for living purposes, storage, or fuel-fired equipment could be protected throughout by a heat-detection system that is arranged to activate in accordance with the 2012 LSC.

## Slide 9: Attic Criteria
Attics shall be of noncombustible or limited-combustible construction.
or
Attics shall be constructed of fire-retardant-treated wood in accordance with NFPA 703, Standard for Fire Retardant-Treated Wood and Fire-Retardant Wood and Fire-Retardant Coatings for Building Materials.
Notes: In attics not used for living purposes, storage, or fuel-fired equipment that are constructed of noncombustible, limited-combustible materials or fire-retardant-treated wood, would not require fire protection by a sprinkler system nor heat-detection system.
NFPA 200 – Standard on Types of Building Construction, Section 4.1.5 and 4.1.6 provide specific definitions of noncombustible and limited-combustible materials, and fire-retardant-treated wood must be in accordance with NFPA 703 - Standard for Fire Retardant-Treated Wood and Fire-Retardant Wood and Fire-Retardant Coatings for Building Materials.
ICF-IID facilities will need to reference these NFPA standard and be able to verify that their attic construction complies with one of these definitions in order to utilize the construction allowance in lieu of fire protection by a sprinkler system or heat-detection system.

## Slide 10: Automatic Sprinkler Not Required
Where an automatic sprinkler system is not required by the LSC, ICF-IID are not subject to these specific attic protection requirements.
Notes: The 2012 LSC requires new ICF-IID facilities to have an automatic sprinkler system installed. CMS considers new ICF-IID as those facilities constructed or with all required pre-construction government approvals after July 5, 2016, which is the effective date the CMS 2012 LSC regulation.
Existing ICF-IID facilities may be required to have an automatic sprinkler system in accordance with LSC extinguishment requirements, construction requirements or other requirements. Existing ICF-IID facilities that are not required by the LSC to have an automatic sprinkler system, are not subject to the new NFPA attic fire protection requirement.

## Slide 11: Compliance
If an ICF-IID is required by the LSC to have a sprinkler system and attic fire protection requirements are not met, immediately:
  Assess attic space for use and contents
  Determine attic construction materials
  Take steps needed to achieve compliance
State Survey Agencies will survey to determine compliance with this requirement starting July 5, 2019.
Notes: As previously discussed, the LSC requires new ICF-IID facilities to have an automatic sprinkler protection system, and existing certified ICF-IID should already know if the LSC requires a sprinkler system at their facility.
If an ICF-IID is required by the LSC to have a sprinkler system and the new attic fire protection requirements are not being met, the facility should:
assess the attic space to determine whether it is being used for living purposes, storage or fuel-fired equipment;
determine whether the attic is constructed with non-combustible, limited-combustible or fire-retardant-treated wood
Once this information is determined, the facility can determine the option best suited for them to come into compliance.
As required by regulation, the CMS State Survey Agencies will begin to survey for compliance with the new NFPA attic fire protection requirements at upcoming annual surveys beginning July 5, 2019. CMS will not perform targeted surveys in advance of the annual surveys to determine compliance with this specific requirement. As the attic fire protection requirement is a standard in 483.470, the State Survey Agency should cite non-compliance at the standard-level. However, surveyors may determine that specific circumstances at a facility warrant a condition-level deficiency.
I must emphasize that ICF-IID facilities are expected to be in compliance with the new NFPA attic as of July 5, 2019. Therefore, any ICF-IID not currently incompliance should take immediate action to achieve substantial compliance.

## Slide 12: Life Safety Code Waiver
ICFs-IID are permitted to meet either the
Residential Board and Care Occupancies chapter or the Health Care Occupancy chapters of the LSC.
For ICFs-IID that meet the Health Care Occupancy chapters of the LSC:
  If the requirement for the attic fire protection would result in unreasonable hardship for the ICF-IID, then CMS may waive specific provisions of the LSC, but only if the waiver does not adversely affect the health and safety of clients.
Notes: ICF-IIDs are permitted to be classified as either Residential Board and Care Occupancies or Health Care Occupancies in accordance with the LSC. In instances where ICF-IID meet the Health Care Occupancy requirements, regulation under 483.470(j)(5)(v)(B) would permit the State Survey Agency to recommend a waiver of the attic fire protection requirement, for periods deemed appropriate, if it achieving compliance would result in unreasonable hardship and the waiver would not adversely affect the health and safety of patients.
A waiver could be requested by the ICF-IID as part of a CMS certification survey Plan of Correction. The State Survey Agency will forward requests it recommends to the CMS Regional Office, who will make the final determination whether to approve the waiver request.

## Slide 13: Summary
In conclusion, this presentation reviewed the following:
  Regulatory requirements for the attic fire safety requirement
  Attic protection requirements for occupied or used attic spaces
  Attic protection requirements for unoccupied or unused attic spaces
  Health care occupancy waiver
Notes: In conclusion, this presentation provided information to assist with the understanding of:
The CMS regulatory requirements associated with attic fire protection;
The NFPA fire protection requirements associated with attics that are occupied and those that are unoccupied or unused; and
The ability for certain ICF-IID facilities to request a LSC waiver.

## Slide 14: Questions
Questions related to the life safety code requirements for ICF/IID can be submitted to the following mailboxes:
QSOG_ICFIID@cms.hhs.gov
&
QSOG_LifeSafetyCode@cms.hhs.gov
Notes: I hope that you have found this presentation informative and that it provided you with a better understanding of the CMS and NFPA requirements associated with the new attic fire protection requirements.
If you have any questions you would like to ask regarding the new NFPA attic fire protection requirements for ICF-IIDs, please feel free to send them to the following email addresses:
QSOG_ICFIID@cms.hhs.gov
&
QSOG_LifeSafetyCode@cms.hhs.gov
Thank you for attending this presentation and for your continued efforts to maintain compliance.